SECTION 27 21 29

POWER SUPPLIES

Copyright 2024Allied Telesis Incorporated - All rights reserved.

<THIS ENTIRE DOCUMENT can be edited to meet specific client and project needs>

- GENERAL

  - SECTION INCLUDES

    - POWER SUPPLIES

      - AT-IE048-240

  - GENERAL REQUIREMENTS

    - The specified power supply product shall be a power supply platform designed for use withan approved Allied Telesis network device.

  - PROPOSAL SUBMITTALS

    - Follow all requirements noted on the Form of Proposal and head-end bidding documents if provided.

    - System Integrator shall provide the following submittals as part of the project submittal package.

    - Complete product and technical data specification data sheets that include all material and equipment and shall be available freely online. Include any installation manual(s) and warranty information.

      - A bill of material of all equipment with counts, part numbers and manufacturer.

      - Software manufacturer, name, and version.

      - New or additional feature licenses.

      - Third-party software if required by the project.

      - Locations and details for all components to be installed under this scope of work.

      - Placement Diagram showing the proposed location of all system hardware devices.

      - System Calculation of all network bandwidth and power requirements to ensure proper planning of networking infrastructure, based on the requirements outlined within these specifications.

    - features to meet or exceed the products named before bid submittal and with pre-approval.

  - PRE-CONSTRUCTION SUBMITTALS

    - After the project award, the contractor shall provide any additional submittals not included in their original pre-bid submittal package.

    - Product Data: For each type of product indicated. Include dimensions and data on features, performance, electrical characteristics, ratings, and finishes.

    - Location Drawings: For network infrastructure. Include plans, elevations, sections, details, and attachments to other work.

  - CLOSEOUT SUBMITTALS

    - After project completion, the contractor shall provide additional project close out submittals required.

    - Operation and Maintenance Data: For switches, routers, power supplies, access points, media converters, small form factor pluggables, to include in emergency, operation, and maintenance manuals.

    - Lists of spare parts and replacement components recommended to be stored at the site for ready access (if applicable).

    - Complete hardcopy printout and electronic copy from the equipment manufacturer which outlines system and equipment configuration, includes model number, IP address, and MAC address at the time of installation and other system settings.

  - DISCLOSURE OF NON-CONFORMING EQUIPMENT

    - Project owner desires to make an informed decision regarding the Contractor's proposed project approach, mobilization, staging and overall implementation schedule of tasks.

    - The contractor is required to disclose, separate from any cut or advertising sheets, any functional, operational, or electrical requirements of these specifications that they are not able to perform, and/or which fall outside the scope of their quotation.

  - ONGOING SUPPORT AND WARRANTY

    - The product manufacturer shall provide a 5-year warranty for the power supply, to be free of defects in material and workmanship.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver and store products in manufacturer's unopened packaging bearing the brand name and manufacturer's identification until ready for installation.

    - Handling: Handle materials to avoid damage.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

  - SEQUENCING

    - Ensure that products of this section are supplied to affected trades in time to prevent interruption of construction progress.

  - RELATED SECTIONS

    - Division 28 - Electrical.

  - REFERENCES

    - Code of Federal Regulations (CFR).

    - Institute of Electrical and Electronics Engineers (IEEE):

      - 802.3 Ethernet Standards.

    - International Electrotechnical Commission (IEC).

    - Federal Communications Commission (FCC):

      - FCC Rules and Regulation of Title 47 of CFR Part 15 Subpart B Class A.

    - Underwriters Laboratories (UL):

      - UL listed.

    - United States Military Standard (MIL-STD):

      - MIL-STD-810F - Environmental Engineering Considerations and Laboratory Tests.

    - National Defense Authorization Act (NDAA):

      - A series of United States of America Federal Laws that include equipment sourcing guidance and standards.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:

      - Allied Telesis Incorporated, which is located at: 10521 19th Ave SE, Suite 200 Everett, WA 98208

      - Phone: (408) 519-8700

      - Web: https://www.alliedtelesis.com/

    - Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 - Product Requirements.

  - POWER SUPPLIES

    - AT-IE048-240

      - EQUIPMENT

        - Manufacturer: 	Allied Telesis Incorporated

        - Model		AT-IE048-240

        - Alternates: 	None

      - GENERAL SPECIFICATIONS

        - The power supply shall be an AT-IE048-240 model.

        - The power supply features 2 DC output connections.

        - The power supply features 1 AC/DC Input connector

        - The power supply DC output shall be adjustable by TRM screw

        - The power supply shall provide Alarm and DC_OK indicating LEDs for monitoring proper system operation.

      - STATUS INDICATORS

        - DC_OK: Off; Steady green – Power supply is operating normally.

        - ALARM: Off – Power supply is operating normally/ power supply powered off; Steady amber – Output voltage is low compared to set voltage.

      - CONNECTORS

        - Input:

          - Grounding Connector

          - AC/DC Input Connector

          - Remote Controller Connector

        - Output:

          - DC_OK Output Connector

          - DC Output Connector

      - ELECTRICAL SPECIFICATIONS

        - Power characteristics:

          - Input:

            - Voltage:

              - AC: 90-264 Vac

              - DC: 98-350 Vdc

            - Current(typ.): 2.3A@115 Vac, 1.2A@230 Vac

            - Frequency: 45-65Hz or DC

            - Efficiency (typ.): 92%@115 Vac, 94%@230 Vac

            - Power Factor(typ.): 0.98%@115 Vac, 0.93@230 Vac

            - Inrush Current(typ.): 20A@115 Vac, 40A@230 Vac

            - Leakage Current: ≤0.45mA@100 Vac, ≤0.75mA@240 Vac

            - Line Noise Tolerance: 2kV, 50-1000ms, ±0~360˚

          - Output:

            - Voltage(nominal): 52 Vdc

            - Current: 4.6A

            - Peak Current: 4.6A

            - Line Regulation: ≤192mV

            - Load Regulation: ≤300mV

            - Ripple:

              - 0˚C to 70˚C: ≤240mVp-p

              - -25˚C to 0˚C: ≤500mVp-p

              - lo=0 - 30%: ≤750mVp-p

            - Ripple Noise:

              - 0˚C to 70˚C: ≤300mVp-p

              - -25˚C to 0˚C: ≤580mVp-p

              - lo=0 - 30˚C: ≤750mVp-p

            - Line Noise Tolerance: 2kV, 50-1000ms, ±0~360˚

            - Temperature Coefficient:

              - 0˚C to 70˚C: ≤480mV

              - -25˚C to 0˚C: ≤600mV

            - Voltage Accuracy Maximum:

              - 0˚C to 70˚C: ≤486mV

              - -25˚C to 0˚C: ≤606mV

            - Drift: ≤192mV

            - Start-up Time: ≤750ms

            - Hold-up Time(typ.): 20ms

            - Output Voltage Adjustment Range: 48.0-55.0Vdc

            - Default Output Voltage Setting: 52.0Vdc±1%

            - Protection:

              - Over current: >101% of peak current

              - Over voltage: 58.1-68.0Vdc

              - Over temp: Yes

      - MECHANICAL SPECIFICATIONS

        - Enclosure Dimensions: 1.97” x 4.61” x 4.88” (50 mm x 117 mm x 124 mm)

        - Finish: Module shall be constructed of a metal enclosure.

        - Weight: 1.98 lbs. / 900 g

      - ENVIRONMENTAL SPECIFICATIONS

        - MTBF: >1,310,000 Hrs @25˚ C, 1,040,000 Hrs @30˚ C

        - Operating Temp: -25˚ C to 70˚ C

        - Storage Temp: –40˚ C to 85˚ C

        - Relative Humidity: 20 to 90% (non-condensing)

        - Protection: IP20

      - REGULATORY AGENCIES/APPROVALS AND LISTINGS

        - EMI (Emissions):

          - CISPR 32, class B

          - EN 55011, class B

          - EN 55032, class B

          - FCC 47 CFR Part 15, subpart B, class B

          - VCCI, class B

        - EMC (Immunity):

          - EN55035

          - IEC 61000-3-2, class A

          - IEC 61000-3-3

          - IEC 61000-4-2, contact discharge: level 4

          - IEC 61000-4-3, level 3

          - IEC 61000-4-4, level 4

          - IEC 61000-4-5, line-to-line: level 3;line-to-earth: level 4

          - IEC 61000-4-6, level 3

          - IEC 61000-4-8, level 4

          - IEC 61000-4-11, 30% reduction for 500ms 60% reduction for 200ms

        - Safety:

          - CAN/CSA C22.2 No. 62368-1

          - EN/IEC/UL 62368-1

          - UL 508

        - Compliance Marks:

          - CE

          - cULus

          - RCM

          - UL

        - Environmental Compliance

          - RoHS

          - China-RoHS

          - WEEE

        - Physical:

          - Shock: Non-operating: 20g, 11ms, half-sine (packaged)

          - Vibration: Non-operating: 2g @10~55Hz (DIN rail)

          - Hazardous Location: ANSI/ISA12.12.01 class I, division 2, groups A, B, C and D

- EXECUTION

  - PREPARATION

    - System Integrator: Confirm the solution proposal planning and design with the installing contractor.