Hanwha Vision is a leading supplier of advanced video surveillance solutions for IP-video, analog and hybrid systems. Building on the company's history of innovation, Hanwha Vision is dedicated to providing systems solutions with the highest levels of performance, reliability and cost-efficiency. Hanwha Vision is committed to the continued development of innovative systems products for professional security applications.

For additional information, visit https://www.hanwhavision.com/en/, https://hanwhavisionamerica.com

- PRODUCTS

  - SUMMARY

    - Section includes a biometric reader and door controller with Ethernet network connectivity

    - Product - An IP enabled biometric reader and door controller, capable of scanning and registering fingerprints and RFID cards, managing users and controlling access.

REFERENCE

- Standards

- IEEE 802.3 Ethernet Standards

- FCC - Code of Federal Regulations, Title 47, Part 15, Class B

- ANSI / IEC60529 – Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP67

- IEC 62262 - Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts IK08

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com
support@supremainc.com

Model(s): BioEntry W2

Alternates: NONE

DESCRIPTION

- The biometric reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning fingerprints and RFID cards, managing users and controlling access.

FEATURES

- Access control and time attendance device

- Dual-band RF reading(RM&MIFARE), HID multiCLASS support

- IP67, Dust & Water Proof

- IK08, Vandal Proof

- Mullion type form-factor

- Quad Core 1.2GHz

- Live Finger Detection (LFD)

- NIST MINEX certified and compliant

- TCP/IP, PoE, RS-485, Wiegand, TTL, Relay, Tamper

- Built-in card reader with card options (125 KHz EM/HID Prox, 13.56 MHz MIFARE/DESFire/DESFire EV1/FeliCa/NFC/iCLASS(SEOS))

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| Credential | Biometric | Fingerprint |
|  | RF Option | BEW2-OAP: 125kHz EM, HID Prox & 13.56Mhz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, iCLASS SEOS, NFC, ISO14443A, ISO15693 |
|  | RF read range* | MIFARE/DESFire/EM/HID Prox/iCLASS/ISO15693: 50 mm, FeliCa: 30 mm * RF read range will vary depending on the installation environment. |
| General | CPU | 1.2 GHz Quad Core |
|  | Memory | 2GB Flash + 256 MB RAM |
|  | LED | Multi-color |
|  | Sound | Buzzer |
|  | Operating temperature | -20°C ~ 50°C |
|  | Storage temperature | -40°C ~ 70°C |
|  | Operating humidity | 0% ~ 80%, non-condensing |
|  | Storage humidity | 0% ~ 90%, non-condensing |
|  | Dimension (W x H x D) | 50 mm x 172 mm x 43.5 mm (Bottom) / 38.2 mm (Top) |
|  | Weight | Device: 251g |
|  |  | Bracket: 43g (Including washer and bolt) |
|  | IP rating | IP67 |
|  | IK rating | IK08 |
|  | Certificates | CE, FCC, KC, RoHS, REACH, WEEE |
| Fingerprint | Image dimension | 272 x 320 pixels |
|  | Image bit depth | 8bit, 256 grayscale |
|  | Resolution | 500 dpi |
|  | Template | SUPREMA / ISO 19794-2 / ANSI 378 |
|  | Extractor / Matcher | MINEX certified and compliant |
|  | LFD | Supported |
| Capacity | Max. User (1:1) | 500,000 |
|  | Max. User (1:N) | 100,000 |
|  | Max. Template (1:1) | 1,000,000 |
|  | Max. Template (1:N) | 200,000 |
|  | Max. Text Log | 1,000,000 |
| Interface | Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |
|  | RS-485 | 1ch Host or Slave (Selectable) |
|  | Wiegand | 1ch Input or Output (Selectable) |
|  | TTL input | 2ch Input |
|  | Relay | 1 Relay |
|  | PoE | Supported (IEEE802.3af compliant) |
|  | Tamper | Supported |
| Electrical | Power | Voltage: DC 12V Current: Max. 600 mA |
|  | Switch input VIH | Min. 3V Max. 5V |
|  | Switch input VIL | Max. 1V |
|  | Switch Pull-up resistance | 4.7kΩ (The input ports are pulled up with 4.7kΩ.) |
|  | Wiegand output VOH | More than 4.8V |
|  | Wiegand output VOL | Less than 0.2V |
|  | Wiegand output Pull-up resistance | Internally pulled up with 1 kΩ |
|  | Relay | Voltage: Max. 30VDC Current: 1A |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.

- The device shall be stored in an environment where humidity is in the range of 0% - 90%, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20°C - 50°C.

- The device shall be installed in an environment where humidity is in the range of 0% - 80%, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

Keep at least 30 cm distance between the devices when install multiple devices.

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION

8