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[bookmark: _Toc334350683]Hanwha Vision is a leading supplier of advanced video surveillance solutions for IP-video, analog and hybrid systems. Building on the company's history of innovation, Hanwha Vision is dedicated to providing systems solutions with the highest levels of performance, reliability and cost-efficiency. Hanwha Vision is committed to the continued development of innovative systems products for professional security applications.

For additional information, visit https://www.hanwhavision.com/en/, https://hanwhavisionamerica.com



PART  1  PRODUCTS
1.01 SUMMARY
A. Section includes a biometric reader and door controller with Ethernet network connectivity
B. Product - An IP enabled biometric reader and door controller, capable of scanning and registering fingerprints and RFID cards, managing users and controlling access. 

[bookmark: _Toc173721624]REFERENCE
1. Standards
1. IEEE 802.3 Ethernet Standards
2. FCC - Code of Federal Regulations, Title 47, Part 15, Class B
3. ANSI / IEC60529 – Degrees of Protection Provided by Enclosures
a. International Electrotechnical Commission (IEC) – Ingress Protection Rating IP67
4. IEC 62262 - Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts IK08

QUALIFICATIONS
1. Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.
Installers shall be trained by the Manufacturer to install, configure and commission the access control system.


END OF SECTION

PART 2 - PRODUCTS
EQUIPMENT 
1. Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com
support@supremainc.com
Model(s): BioEntry W2 
Alternates: NONE

DESCRIPTION
1. The biometric reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning fingerprints and RFID cards, managing users and controlling access.

FEATURES
1. Access control and time attendance device
1. Dual-band RF reading(RM&MIFARE), HID multiCLASS support
1. IP67, Dust & Water Proof
1. IK08, Vandal Proof
1. Mullion type form-factor
1. Quad Core 1.2GHz
1. Live Finger Detection (LFD)
1. NIST MINEX certified and compliant 
1. TCP/IP, PoE, RS-485, Wiegand, TTL, Relay, Tamper 
1. Built-in card reader with card options (125 KHz EM/HID Prox, 13.56 MHz MIFARE/DESFire/DESFire EV1/FeliCa/NFC/iCLASS(SEOS))

SPECIFICATIONS
	Category
	Feature
	Specification

	Credential
	Biometric
	Fingerprint

	
	RF Option
	BEW2-OAP: 125kHz EM, HID Prox & 13.56Mhz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, iCLASS SEOS, NFC, ISO14443A, ISO15693

	
	RF read range*
	MIFARE/DESFire/EM/HID Prox/iCLASS/ISO15693: 50 mm, FeliCa: 30 mm

* RF read range will vary depending on the installation environment.

	General
	CPU
	1.2 GHz Quad Core

	
	Memory
	2GB Flash + 256 MB RAM

	
	LED
	Multi-color

	
	Sound
	Buzzer

	
	Operating temperature
	-20°C ~ 50°C

	
	Storage temperature
	-40°C ~ 70°C

	
	Operating humidity
	0% ~ 80%, non-condensing

	
	Storage humidity
	0% ~ 90%, non-condensing

	
	Dimension (W x H x D)
	50 mm x 172 mm x 43.5 mm (Bottom) / 38.2 mm (Top)

	
	Weight
	Device: 251g

	
	
	Bracket: 43g (Including washer and bolt)

	
	IP rating
	IP67

	
	IK rating
	IK08

	
	Certificates
	CE, FCC, KC, RoHS, REACH, WEEE

	Fingerprint 
	Image dimension
	272 x 320 pixels

	
	Image bit depth 
	8bit, 256 grayscale

	
	Resolution
	500 dpi

	
	Template
	SUPREMA / ISO 19794-2 / ANSI 378

	
	Extractor / Matcher
	MINEX certified and compliant 

	
	LFD
	Supported

	Capacity
	Max. User (1:1)
	500,000

	
	Max. User (1:N)
	100,000

	
	Max. Template (1:1)
	1,000,000

	
	Max. Template (1:N)
	200,000

	
	Max. Text Log
	1,000,000

	Interface
	Ethernet
	Supported (10/100 Mbps, auto MDI/MDI-X)

	
	RS-485
	1ch Host or Slave (Selectable)

	
	Wiegand
	1ch Input or Output (Selectable)

	
	TTL input
	2ch Input

	
	Relay
	1 Relay

	
	PoE
	Supported (IEEE802.3af compliant)

	
	Tamper
	Supported

	Electrical
	Power
	Voltage: DC 12V 
Current: Max. 600 mA

	
	Switch input VIH
	Min. 3V
Max. 5V

	
	Switch input VIL
	Max. 1V

	
	Switch Pull-up resistance
	4.7kΩ (The input ports are pulled up with 4.7kΩ.)

	
	Wiegand output VOH
	More than 4.8V

	
	Wiegand output VOL
	Less than 0.2V

	
	Wiegand output Pull-up resistance
	Internally pulled up with 1 kΩ

	
	Relay
	Voltage: Max. 30VDC
Current: 1A



END OF SECTION

PART 3 - EXECUTION
INSTALLER
1. Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION
1. Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.
IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE
1. The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.
1. The device shall be stored in an environment where humidity is in the range of 0% - 90%, non-condensing.

INSTALLATION
1. The device shall be installed in an environment where temperature is in the range of -20°C - 50°C. 
1. The device shall be installed in an environment where humidity is in the range of 0% - 80%, non-condensing.
1. All wires shall be run through conduit to prevent failure caused by rodent damage.
Connections between card readers and a door controller shall not exceed 100 meters.
All peripheral devices shall be grounded.
Keep at least 30 cm distance between the devices when install multiple devices.

EXAMINATION
1. All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION
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