GUIDE SPECIFICATION
MasterFormat 2014: Section 28 23 29
MasterFormat 2016: Section 28 2x xx
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[bookmark: _Toc334350683]Hanwha Techwin is a global leading supplier of solutions for IP and analog video surveillance. Building on the company's history of innovation, Hanwha Techwin is dedicated to providing systems solutions with the highest levels of performance, reliability and cost-effectiveness. Hanwha Techwin is committed to the continued development of innovative systems products for professional security applications.

For additional information, visit http://www.hanwha-security.com/ 



Network I/O Box

[bookmark: _Toc334350689]
[bookmark: _GoBack]DIVISION 28 – ELECTRONIC SAFETY AND SECURITY
[bookmark: _Toc334350690]
Notes to Specifier:
[bookmark: _Toc334350691]1.  Where several alternative parameters or specifications exist, or where, the specifier has the option of inserting text, such choices are presented in <bold text>.
2.  Explanatory notes and comments are presented in colored text.

	
Important:  See further notes on the following page.

Important Note to Security Systems Specifiers


CSI MasterFormat 2016 incorporates numerous significant changes affecting electronic safety and security. This document is written to provide flexibility in using either format, although adoption of MasterFormat 2016 is encouraged. The following is a guide to the MasterFormat numbers relevant to the product referenced in this specification.

Primary Specification Area:
MasterFormat 2014:
28 20 00 	Electronic Surveillance
28 23 00 	Video Surveillance
	28 23 29	Video Surveillance Remote Devices and Sensors
MasterFormat 2016:
	28 20 00	Video Surveillance
	28 2x xx	Surveillance Cameras
	28 2x xx	IP Cameras

Related Requirements:
MasterFormat 2014:
	27 20 00	Data Communications 
	28 23 13	Video Surveillance Control and Management Systems
	28 23 16	Video Surveillance Monitoring and Supervisory Interfaces
	28 23 19	Digital Video Recorders and Analog Recording Devices
	28 23 23	Video Surveillance Systems Infrastructure

MasterFormat 2016
	27 15 01.xx	Video Surveillance Communications Conductors and Cables 
	27 20 00 	Data Communications 
	28 05 xx.xx	PoE Power Sources for Electronic Safety and Security 
	28 05 xx	Storage Appliances for Electronic Safety and Security 
	28 05 xx.xx	Network Video Recorders 
	28 05 xx	Cyber Requirements for Electronic Safety and Security
	28 05 xx	Safety and Security Network Communications Equipment 
	28 2x 00	Video Management System

NETWORK I/O BOX

PART  1   GENERAL
1.01 SUMMARY
A. [bookmark: _Toc334350692]Section includes a Network I/O Box
B. [bookmark: _Toc334350693]Product - A Network I/O box with 4 configurable I/O ports and Audio in/out ports
C. [bookmark: _Toc334350694]Related Requirements

Refer to MasterFormat notes at the beginning of this document to select requirements specific to the MasterFormat version being used in the specification.

1.02 REFERENCES
A. Abbreviations
1. AGC		Auto Gain Control
2. AES		Advanced Encryption Standard
3. API		Application Programming Interface
4. ARP		Address Resolution Protocol
5. AWB		Auto White Balance
6. BLC		Back light compensation
7. CBR		Constant Bit Rate
8. CVBS		Composite Video Blanking and Sync
9. DHCP		Dynamic Host Configuration Protocol
10. DNR		Digital Noise Reduction
11. DNS		Domain Name Server
12. DDNS		Dynamic Domain Name Server
13. DSCP		Differentiated Services Code Point
14. fps		frames per second
15. FTP		File Transfer Protocol
16. GOV		Group of Video
17. GUI		Graphical User Interface
18. HD		High Definition
19. HTTP		Hypertext Transfer Protocol
20. HTTPS		Secure HTTP
21. ICMP		Internet Control Message Protocol
22. IGMP		Internet Group Management Protocol
23. IP		Internet Protocol
24. IR		Infrared
25. JPEG		Joint Photographic Experts Group
26. LAN 		Local Area Network
27. LED		Light Emitting Diode
28. LDC		Lens Distortion Correction
29. LLDP		Link Layer Discovery Protocol
30. LPR		License Plate Recognition
31. MJPEG		Motion JPEG
32. MP		Megapixel
33. MPEG		Moving Pictures Experts Group
34. NAS		Network Attached Storage
35. NTP		Network Time Protocol
36. NVR		Network Video Recorder
37. PIM-SM	Protocol Independent Multicast-Sparse Mode
38. PoE		Power over Ethernet
39. PPPoE		Point to Point Protocol over Ethernet
40. QoS		Quality of Service
41. RTP		Real-Time Transport Protocol
42. RTCP		Real-Time Control Protocol
43. RTSP		Real-Time Streaming Protocol
44. SDK		Software Development Kit
45. SFP		Small Form factor Pluggable
46. SMTP		Simple Mail Transfer Protocol
47. SNMP		Simple Network Management Protocol
48. SSDR		Super Smart Dynamic Range
49. SSNR		Super Smart Noise Reduction
50. SSL		Secure Sockets Layer
51. TCP		Transmission Control Protocol
52. UDP		User Datagram Protocol
53. UPnP		Universal Plug and Play
54. VBR		Variable Bit Rate
55. VMS		Video Management System
56. WDR		Wide Dynamic Range

B. Reference Standards
1. Network - IEEE
a. 802.3 Ethernet Standards
b. 802.1x  Port-based Network Access Control
c. IPv4 IP addressing version 4
d. IPv6 IP addressing version 6
2. EMC & Safety
a. FCC 47 CFR Part 15 Subpart B
1) ANSI C63.4-2014 Class A
b. IC Regulation ICES-003:2016
1) ANSI C63.4-2014 Class A
c. CE EMC-Directive 2014/30/EU
1) EN 55032:2012/ac:2013 Class A
2) EN 50130-4:2011+A1:2014
d. VCCI-CISPR 32: Class A
e. AS/NZS CISPR32:2015 Class A
f. UL 62368-1, 2nd Ed., Issue Date: 2014-12-01
1.03 SUBMITTALS
A. Product Data
1. Manufacturer’s printed or electronic data sheets
2. Manufacturer’s installation and operation manuals
3. Warranty documentation

1.04 QUALIFICATIONS
A. Manufacturer shall have a minimum of five years’ experience in producing IP video equipment.
B. Installers shall be trained and authorized by the Manufacturer to install, integrate.

1.05 DELIVERY, STORAGE AND HANDLING
A. Deliver the camera in the manufacturer’s original, unopened, undamaged container with identification labels intact.
B. Store the camera in a temperature environment specified in section 2.04 Detailed Specification, protected from mechanical and environmental conditions as designated by the manufacturer.

1.06 WARRANTY, LICENSING AND SUPPORT
A. Manufacturer shall provide at least a limited 3 year warranty for the product to be free of defects in material and workmanship.
B. Manufacturer shall provide embedded camera video analytics free of license charges.

END OF SECTION
PART  2 
 PRODUCTS
2.01 EQUIPMENT
A. Manufacturer: 	Hanwha Techwin 
http://www.hanwha-security.com/
B. Model		SPM-4210
C. Alternates: 		None

2.02 GENERAL DESCRIPTION
A. Configurable Input/Output Control – The device shall have the following properties relating to the input/output signal control
1. The device shall have 4 configurable input/output ports
a. 4 ports shall be able to configured as input or output signal
b. Each ports shall be able to configured as normal open and normal close
c. 12V DC output, max load 50mA will be supported
2. The device shall have 1 audio input and 1 audio output ports
3. The device shall have 1 RJ45 network port 
B. The device shall possess the following further characteristics:
1. Built-in web server, accessed via non-plugin browsers including Google Chrome, IE11, MS Edge, Mozilla Firefox and Apple Safari.
2. PoE capable

2.03 DEVICE SOFTWARE
A. The device shall have a built in web server which supports non-plugin browsers including Google Chrome, IE11, MS Edge, Mozilla Firefox and Apple Safari from a PC or Mac. 
B. The web viewer shall provide a web user interface to access to the following functions:
1. Input/Output port configuration
2. Audio In/Out setting
3. Date and time
4. Network settings and IP version
a. IP filtering
b. SSL, including certificate management
c. 802.1x authentication
d. Auto IP configuration
C. Client requirements
1. Acceptable Operating Systems:	Windows 7 / 8.1 / 10, MAC OS X 10.12, 10.13, 10.14
2. Acceptable browsers:		
a. Non-plugin WebViewer	Google Chrome, IE11, MS Edge,
Mozilla Firefox (Window 64bit only), Safari (Mac OS X only)

2.04 DETAILED SPECIFICATIONS
A. [bookmark: _Toc173721624]Operational Functions (Alarms available when the device is connected to Wisenet PTZ Plus cameras)
1. Alarm I/O			Configurable Input / Output 4ea
2. Alarm Triggers			Alarm input
3. Audio I/O			Audio in : Selectable (mic in/line in)
Audio out : Line out, Max. Output level : 1Vrms
4. Internal Memory		4G RAM, 256MB Flash
B. Network
1. Connectivity – 10/100 Base-T Ethernet via RJ-45 connector
2. Protocol
a. IP v4 / v6, TCP, UDP
b. Configuration: DHCP, LLDP
c. Web service: HTTP, HTTPS
d. Network Service: ARP, Bonjour, DNS, ICMP, NTP, PIM-SM, SNMP v1/2c/3 – MIB-2, UPnP
e. Media: RTP, RTCP, RTSP
f. Remote Access: PPPoE
3. Security Feature
a. User password protection
b. The device shall not provide a manufacture default password. Default password change shall be required to access the camera.
c. A minimal level of password complexity shall be required by the camera.
d. The camera shall not have a manufacture back-door password.
e. The manufacturer shall provide a tool that provides the ability to make password changes to multiple cameras at the same time. 
f. IP address filtering – List of allowed or blocked IP addresses
g. HTTPS(SSL) login authentication
h. HTTPS(SSL) secured communication
i. Digest login authentication
j. User access log 
4. Discovery – The manufacturer shall offer a discovery program to identify all devices of them on the network. 
5. Configuration – The manufacturer shall offer a configuration program that remotely allows users to change settings on multiple cameras simultaneously. 
6. Firmware upgrade – The manufacturer shall offer a program capable of upgrading multiple cameras at the same time (not requiring access to individual cameras).
C. Electrical
1. Power
a. Input Voltage / Current	PoE (IEEE 802.3af, Class3)
b. Power Consumption	PoE : Max. 4.5W

D. Mechanical And Environmental
1. Color				White 
2. Dimensions 			143mm x 73mm x 27.3mm
3. Weight 				171 g
4. Temperature 		
a. Operating 			-40°C ~ +60°C (-40°F ~ +140°F)
b. Storage  			-50°C ~ +60°C (-58°F ~ +140°F)
5. Humidity			Less than 90% RH(Non-condensing)

END OF SECTION


PART  1    EXECUTION
1.01 INSTALLERS
A. Contractor personnel shall comply with all applicable state and local licensing requirements.

1.02 PREPARATION
A. The network design and configuration shall be verified for compatibility and performance with the camera(s).
B. Network configuration shall be tested and qualified by the Contractor prior to camera installation.
C. All firmware found in products shall be the latest and the most up-to-date provided by the manufacturer, or of a version as specified by the provider of the VMS or NVR. 
D. All equipment requiring users to log on using a password shall be configured with user/site-specific password/passwords. No system/product default passwords shall be allowed.

1.03 INSTALLATION
A. The contractor shall carefully follow instructions in documentation provided by the manufacturer to insure all steps have been taken to provide a reliable, easy-to-operate system.
B. All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.
C. Before permanent installation of the system, the contractor shall test the system in conditions simulating the final installed environment.

1.04 STORAGE
A. The hardware shall be stored in an environment where temperature and humidity are in the range specified by the manufacturer.
 
END OF SECTION
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