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[bookmark: _Toc334350683]Hanwha Techwin is a global leading supplier of solutions for IP and analog video surveillance. Building on the company's history of innovation, Hanwha Techwin is dedicated to providing systems solutions with the highest levels of performance, reliability and cost-effectiveness. Hanwha Techwin is committed to the continued development of innovative systems products for professional security applications.

For additional information, visit http://www.hanwha-security.com/ 



2M 32x NETWORK EXPLOSION PROOF PTZ CAMERA
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DIVISION 28 – ELECTRONIC SAFETY AND SECURITY
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Notes to Specifier:
[bookmark: _Toc334350691]1.  Where several alternative parameters or specifications exist, or where, the specifier has the option of inserting text, such choices are presented in <bold text>.
2.  Explanatory notes and comments are presented in colored text.

	
Important:  See further notes on the following page.

Important Note to Security Systems Specifiers


CSI MasterFormat 2016 incorporates numerous significant changes affecting electronic safety and security. This document is written to provide flexibility in using either format, although adoption of MasterFormat 2016 is encouraged. The following is a guide to the MasterFormat numbers relevant to the product referenced in this specification.

Primary Specification Area:
MasterFormat 2014:
28 20 00 	Electronic Surveillance
28 23 00 	Video Surveillance
	28 23 29	Video Surveillance Remote Devices and Sensors
MasterFormat 2016:
	28 20 00	Video Surveillance
	28 2x xx	Surveillance Cameras
	28 2x xx	IP Cameras

Related Requirements:
MasterFormat 2014:
	27 20 00	Data Communications 
	28 23 13	Video Surveillance Control and Management Systems
	28 23 16	Video Surveillance Monitoring and Supervisory Interfaces
	28 23 19	Digital Video Recorders and Analog Recording Devices
	28 23 23	Video Surveillance Systems Infrastructure

MasterFormat 2016
	27 15 01.xx	Video Surveillance Communications Conductors and Cables 
	27 20 00 	Data Communications 
	28 05 xx.xx	PoE Power Sources for Electronic Safety and Security 
	28 05 xx	Storage Appliances for Electronic Safety and Security 
	28 05 xx.xx	Network Video Recorders 
	28 05 xx	Cyber Requirements for Electronic Safety and Security
	28 05 xx	Safety and Security Network Communications Equipment 
	28 2x 00	Video Management System

2M 32x NETWORK IR EXPLOSION PROOF PTZ CAMERA

PART  1   GENERAL
1.01 SUMMARY
A. [bookmark: _Toc334350692]Section includes a 2M IP camera with explosion-proof certificates in a stainless housing and PTZ capability. 
B. [bookmark: _Toc334350693]Product - A 2M IP camera, with multi-streaming (H265, H.264 and MJPEG) capability with IR illuminator
C. [bookmark: _Toc334350694]Related Requirements

Refer to MasterFormat notes at the beginning of this document to select requirements specific to the MasterFormat version being used in the specification.

1.02 REFERENCES
A. Abbreviations
1. AGC		Auto Gain Control
2. AES		Advanced Encryption Standard
3. AI		Artificial Intelligence
4. API		Application Programming Interface
5. ARP		Address Resolution Protocol
6. AWB		Auto White Balance
7. BLC		Back light compensation
8. CBR		Constant Bit Rate
9. CVBS		Composite Video Blanking and Sync
10. DHCP		Dynamic Host Configuration Protocol
11. DNR		Digital Noise Reduction
12. DNS		Domain Name Server
13. DDNS		Dynamic Domain Name Server
14. DSCP		Differentiated Services Code Point
15. fps		frames per second
16. FTP		File Transfer Protocol
17. GOV		Group of Video
18. GUI		Graphical User Interface
19. HD		High Definition
20. HTTP		Hypertext Transfer Protocol
21. HTTPS		Secure HTTP
22. ICMP		Internet Control Message Protocol
23. IGMP		Internet Group Management Protocol
24. IP		Internet Protocol
25. IR		Infrared
26. JPEG		Joint Photographic Experts Group
27. LAN 		Local Area Network
28. LED		Light Emitting Diode
29. LDC		Lens Distortion Correction
30. LLDP		Link Layer Discovery Protocol
31. LPR		License Plate Recognition
32. MJPEG		Motion JPEG
33. MP		Megapixel
34. MPEG		Moving Pictures Experts Group
35. NAS		Network Attached Storage
36. NTP		Network Time Protocol
37. NVR		Network Video Recorder
38. PIM-SM	Protocol Independent Multicast-Sparse Mode
39. PoE		Power over Ethernet
40. PPPoE		Point to Point Protocol over Ethernet
41. QoS		Quality of Service
42. RTP		Real-Time Transport Protocol
43. RTCP		Real-Time Control Protocol
44. RTSP		Real-Time Streaming Protocol
45. SDK		Software Development Kit
46. SFP		Small Form factor Pluggable
47. SMTP		Simple Mail Transfer Protocol
48. SNMP		Simple Network Management Protocol
49. SSDR		Super Smart Dynamic Range
50. SSNR		Super Smart Noise Reduction
51. SSL		Secure Sockets Layer
52. TCP		Transmission Control Protocol
53. UDP		User Datagram Protocol
54. UPnP		Universal Plug and Play
55. VBR		Variable Bit Rate
56. VMS		Video Management System
57. WDR		Wide Dynamic Range
B. Reference Standards
1. Network - IEEE
a. 802.3 Ethernet Standards
b. 802.1x  Port-based Network Access Control
c. IPv4 IP addressing version 4
d. IPv6 IP addressing version 6
e. QoS Quality of Service
2. Video
a. ISO / IEC 23008-2:2013, MPEG-H Part2 (ITU H.265, HEVC)
b. ISO / IEC 14496–10, MPEG-4 Part 10 ( ITU H.264)
c. ISO / IEC 10918 – JPEG 
d. ONVIF – Profile S / G / T
3. EMC & Safety
a. FCC 47 CFR Part 15 Subpart B
1.) ANSI C63.4-2014 Class A
b. IC Regulation ICES-003:2016
1.) ANSI C63.4-2014 Class A
c. CE EMC-Directive 2014/30/EU
1.) EN 55032:2015 Class A
2.) EN 50130-4:2011+A1:2014
d. VCCI-CISPR 32: Class A
e. AS/NZS CISPR32:2015 Class A
f. UL listed
g. CE EN 50581:2012 (hazardous substances)
4. Ingress Protection and Vandal Resistance
a. IEC 60529:2017 – Degrees of Protection Provided by Enclosures – IP67
b. IEC EN 62262:2005 - Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts : IK10
5. ATEX Directive (Explosion Proof Certificate)
a. CE2460 EX II 2 GD Ex d IIC T6 Gb IP67 Ex tb IIIC T80°C Db
6. IEC 60079-31   Part 31: Equipment dust ignition protection by enclosure 't'
a. Ex DB  IIC T6 Gb
b. Ex tb IIIC T80 ℃ Db
C. Definitions
1. GOV (Group of Video object planes) – A set of video frames for H.264 and H.265 compression, indicating a collection of frames from the initial I-Frame (key frame) to the next I-Frame. GOV consists of two kinds of frames in video surveillance setup: I-Frame and P-Frame.
2. Dynamic GOV – Dynamic assignment of GOV length based on the complexity of the scene to efficiently manage bitrate of the video stream and reduce the storage required. 
3. Multi-exposure wide dynamic range – Operation which automatically adjusts shutter speed to provide a wide range between dark and light areas visible at the same time, preventing backlighting issues. Long exposure is used for dark areas and a short exposure is used in bright areas.
4. Dynamic fps – Dynamic assignment of fps (frames per seconds) based on the movement of object(s) in the scene to efficiently manage bitrate of the video stream and reduce the storage required.
5. WiseStream – Technology that controls quantization parameter, fps, and GOV length in H.265 and H.264 to efficiently manage bitrate of the video stream and reduce the storage required.
1.03 SUBMITTALS
A. Product Data
1. Manufacturer’s printed or electronic data sheets
2. Manufacturer’s installation and operation manuals
3. Warranty documentation
1.04 QUALIFICATIONS
A. Manufacturer shall have a minimum of five years’ experience in producing IP video equipment.
B. Installers shall be trained and authorized by the Manufacturer to install, integrate, test, and commission the system.
1.05 DELIVERY, STORAGE AND HANDLING
A. Deliver the camera in the manufacturer’s original, unopened, undamaged container with identification labels intact.
B. Store the camera in a temperature environment indicated in 2.04 Detailed Specification, protected from mechanical and environmental conditions as designated by the manufacturer.
1.06 WARRANTY, LICENSING AND SUPPORT
A. Manufacturer shall provide a limited 3 year warranty for the product to be free of defects in material and workmanship.
B. Manufacturer shall provide embedded camera video analytics free of license charges.

END OF SECTION
PART  2 
 PRODUCTS
2.01 EQUIPMENT
A. Manufacturer: 	Hanwha Techwin 
http://www.hanwha-security.com/
B. Model		TNU-6322ER
C. Alternates: 		None
2.02 GENERAL DESCRIPTION
A. The explosion proof camera shall have a metal housing which can prevent any inside sparks caused by the electronic components from igniting gases and conductive dust and causing explosion in a hazardous area. The camera shall also have PTZ capability. 
B. Video Compression and Transmission – The camera shall have the following properties relating to the video signals it produces.
1. H.265, H.264 and MJPEG compression, each derived from a dedicated encoder and capable of being streamed independently and simultaneously.
a. H.265 and H.264 – maximum of 30/25fps(60Hz/50Hz) at all resolution
2. MJPEG – maximum of 30/25fps(60Hz/50Hz)
3. The camera shall be able to configure up to 10 independent video stream profiles with differing encoding, quality, frame rate, resolution, and bit rate settings. 
4. The camera shall be able to configure various resolution selections.
a. 16:9 aspect ratio : 	1920 x 1080, 1280 x 720, 800 x 448,640 x 360
b. 4:3 aspect ratio : 	1280 x 960, 1024 x 768, 800 x 600, 640 x 480, 320 x 240
c. 5:4 aspect ratio : 	1280 x 1024, 720 x 576
d. 3:2 aspect ratio : 	720 x 480
5. The camera shall support unicast video streaming up to 20 users.
6. The camera shall support multicast video streaming.
7. The camera shall support multiple video streaming up to 10 profiles 
8. The camera shall be able to configure Dynamic DNS (DDNS). DDNS shall be provided with no additional cost by the manufacturer. 
9. The camera shall provide WiseStream Ⅱ, Dynamic GOV and Dynamic FPS to efficiently manage bit rate of the video stream and reduce storage.
C. Camera – The camera device shall have the following physical and performance properties:
1. IK10 rated for protection against impacts. 
2. Dust proof and water proof (IP67 rated)
3. Explosion proof (ATEX, IECEx)
4. True day/night operation with removable IR cut filter
a. Low light level operation to 0.05 lux at F1.6 in color mode and 0.005 lux at F1.6 in black and white mode.
5. The camera shall be able to produce clear images in highly contrast scenes with multi-exposure wide dynamic range up to 120dB.
6. The camera shall support digital noise reduction using both 2D and 3D noise reduction technology.
7. 32 privacy masking regions utilizing polygons with zoom threshold mosaic option 
D. Intelligence and Analytics – The camera shall have a suite of intelligent analytic functions.
1. Motion detection with 8 definable detection areas with 8 point polygonal zones, and minimum/maximum object size.
2. Detection of logical events of specified conditions from the camera’s video
a. Analytics events : Defocus detection, Directional detection, Fog detection, Face detection,
                             Motion detection, Appear/Disappear, Enter/Exit, Loitering, Tampering,
Audio detection
B. Interoperability – The camera shall be ONVIF Profile S / G and T compliant. 
C. The camera shall possess the following further characteristics:
1. Built-in web server, accessed via non-plugin browsers including Google Chrome, IE11, MS Edge, Mozilla Firefox and Apple Safari.
2. NAS recording option with configurable pre-alarm and post-alarm recording intervals
3. Alarms and notifications
a. alarm notification triggers:
1.) alarm input
2.) Analytics
3.) Network disconnect
b. available notification means upon trigger:
1.) File upload via FTP and e-mail
2.) Notification via e-mail
3.) NAS recording at event triggers
4.) Alarm output
5.) PTZ preset
4. Pixel Counter available in the web viewer. 
5. IP67, IK10, IECEx, ATEX

1.02 CAMERA SOFTWARE
A. The camera shall have a built in web server which supports non-plugin browsers including Google Chrome, IE11, MS Edge, Mozilla Firefox and Apple Safari from a PC or Mac. 
B. The web viewer shall provide a monitoring screen which displays live camera video and simultaneously provides same-screen access to the following functions:
1. Live view window size
2. Resolution setting
3. Image (snapshot) capture
4. Manual recording to NAS
5. Access Playback and Setup menus
C. The web viewer shall provide a playback screen which provides access to the following functions:
1. Search date and time range
2. Search event type
3. Play an event video
4. Set playback speed
5. Play audio if present
6. Generate a backup copy of saved video data
D. The web viewer shall provide a setup screen which provides access to the following configuration settings and functions in the camera:
1. Digital video profile to include compression type, maximum or target bit rate, frame rate, multicast parameters, crop encoding area
2. User profile to include password, access level, authentication
3. Date and time
4. Network settings and IP version
a. DDNS
b. SSL, including certificate management
c. 802.1x authentication
d. Quality of Service settings
e. SNMP to include version selection and settings
f. Auto configuration
5. Video setup
a. Flip / mirror mode
b. Video output type 
c. Privacy zone
6. Audio setup to include source, audio codec type, gain and bit rate.
7. Camera settings to configure image preset, sensor frame capture speed, dynamic range, white balance, back light, exposure, day/night operation, on-screen display, sharpness, contrast, color level and lens distortion correction.
8. Event detection setup to include notification parameters, recording rules, time schedule, tamper protection, motion detection, event triggers
9. System function to include reboot, upgrade, check system and event logs, application (SDK) management
10. View profile information

E. Client requirements
1. Recommend Browser : Chrome
2. Acceptable Browser : Chrome, Safari, Firefox, MS Edge(chromium based)
3. Acceptable Operating Systems:	Windows, MAC, Android, iOS, Chrome
4. Verified Environment:		
a. Windows 10 : Google chrome version 80 above, Firefox version 72 above, 
                               MS Edge version 83 above
b. Mac 10.13/14 : Safari version 11.0.1 above 
※ Decoding performance in web viewer depends on CPU/GPU performance of user

1.03 DETAILED SPECIFICATIONS
A. [bookmark: _Toc173721624]Video
1. Imaging device			1/2.8" 8MP CMOS
2. Image Pixels			1,952(H) x 1,116(V)  total; 1,944(H) x 1,104(V) effective
3. Scanning			Progressive
4. Minimum Illumination		Color: 0.05Lux (F1.6, 1/30sec), 
B/W: 0.005Lux (F1.6, 1/30sec), 0Lux(IR LED on)
B. Lens:			
1. Focal length			4.44~142.6mm(32x) zoom
2. Max. Aperture Ratio		F1.6(Wide)~F4.4(Tele)
3. Field of View			H: 61.8 ˚(Wide) ~ 2.19°(Tele)
V: 36.2 ˚(Wide) ~ 1.24°(Tele)
4. Min. Object Distance		Wide : 1.5m (4.92ft), Tele : 2m (6.56ft)
5. Focus Control			Auto/manual/One shot AF
6. Lens Type			DC Auto Iris
7. Mount Type			Board-in Type
C. Pan & Tilt & Rotate
1. Pan Range			360˚ Endless
2. Pan Speed			0.5˚/sec ~ 80˚/sec
3. Tilt Range			180˚(-90˚~ 90˚)
4. Tilt Speed			0.1˚/sec ~ 60˚/sec
5. Sequence			Preset(300ea), Swing, Group(6ea), Tour, Auto run, Schedule
6. Preset Accuracy		±0.25˚
D. IR Viewable Length			200m (656ft)
E. Operational Functions
1. Camera Title 			Off / On (Displayed up to 85 characters)
a. W/W 			English / Numeric / Special characters
b. China 			English / Chinese / Numeric / Special characters
c. Common			Multi-line (Max. 5), Color (Grey/Green/Red/Blue/Black/White),
Transparency, Auto scale by resolution
2. Direction Indicator		Support
3. Day/Night Setting		Auto (ICR) / Color / B/W / Schedule
4. Backlight Compensation		Off / BLC / HLC / WDR
5. Wide Dynamic Range		120dB
6. Contrast Enhancement		Off / On (SSDR)
7. Digital Noise Reduction		Off / On (SSNR5 : 2D+3D Noise filter)
8. Digital Image Stabilization	Off / On (built-in Gyro sensor)
9. Defog				Support
10. Motion Detection		Off / On (8ea, 8-point polygonal)
11. Privacy Masking		Off / On (6 zones, rectangle)
- Color: Grey / Green / Red / Blue / Black / White
- Mosaic
12. Gain Control			Off / Low / Middle / High
13. White Balance 			ATW / AWC / Manual / Indoor / Outdoor
14. Image Rotation			Flip: Off / On
Mirror: Off / On
Hallway view: 0˚ / 90˚ / 270˚
15. Alarm I/O			Input 1ea / Output 1ea 
16. Alarm Triggers			Alarm Input, Analytics, Network Disconnection
17. Alarm Events			File Upload via FTP and E-mail, Notification via E-mail,
NAS recording at event triggers,
Alarm output, PTZ preset
18. Pixel Counter			Support
19. Intelligent Analytics		Defocus detection, Directional detection, Fog detection,
Face detection, Motion detection, Appear/Disappear,
Enter/Exit, Loitering, Tampering, Virtual line, Audio detection
20. Memory			1024MB RAM, 256MB Flash
21. Water Removal			Support (with Wiper)
F. Video Streams
1. Video compression		H.265, H.264, MJPEG
2. Resolution			1920x1080, 1280x1024, 1280x960, 1280x720, 1024x768,
800 x 600, 800 x 448, 720 x 576, 720x480, 640x480, 640x360
320x240
3. Maximum Framerate
a. H.265 / H.264		Max. 60/50fps(60Hz/50Hz) at all resolutions
b. MJPEG 			Max. 30/25fps(60Hz/50Hz)
4. Smart Codec			Manual Mode (area-based : 5EA)
5. WiseStream Ⅱ			Support
6. Bitrate Control Method		H.265 / H.264: CBR or VBR
MJPEG: VBR
7. Streaming Capability		Multiple streaming (Up to 10 profiles)
8. Streaming method		Unicast / Multicast
9. Simultaneous Users		20 maximum (Unicast)
10. Profile set			Max. 10 ea
11. Interoperability			ONVIF Profile S / G / T, SUNAPI(HTTP API), Open Platform
G. Audio
1. Audio In			Mic-in / Line-in
Supply voltage: 2.5V DC(4mA), Input impedance: 2K Ohm
2. Audio Out			Line out, Max. output level 1Vrms
3. Audio Compression		G.711 / G.726 / AAC Selectable, 
G.711 u-law 8KHz
G.726 (ADPCM) 16 / 24 / 32 / 40Kbps at 8KHz,
AAC-LC: 48Kbps at 16KHz
H. Network
1. Connectivity – Metal Shield RJ-45(10/100BASE-T)
2. Protocol
a. IP v4 / v6, TCP, UDP
b. Configuration: DHCP
c. Web service: HTTP, HTTPS
d. Network Service: ARP, Bonjour, DNS, ICMP, NTP, PIM-SM, SNMP v1/2c/3 – MIB-2, UPnP
e. Media: RTP, RTCP, RTSP
f. Multicast: IGMP
g. Notifications: FTP, SMTP
3. DDNS – The camera shall support DDNS services offered by the manufacturer and others publicly available service offerings
4. QoS – Layer 3 DSCP
5. Security Feature
a. User password protection
b. The device shall not provide a manufacture default password. Default password change shall be required to access the camera.
c. A minimal level of password complexity shall be required by the camera.
d. The camera shall not have a manufacture back-door password.
e. The manufacturer shall provide a tool that provides the ability to make password changes to multiple cameras at the same time. 
f. IP address filtering – List of allowed or blocked IP addresses
g. HTTPS(SSL) login authentication
h. HTTPS(SSL) secured communication
i. Digest login authentication
j. User access log 
k. 802.1x authentication(EAP-TLS, EAP-LEAP)
6. Discovery – The manufacturer shall offer a discovery program to identify all devices of them on the network. 
7. Configuration – The manufacturer shall offer a configuration program that remotely allows users to change settings on multiple cameras simultaneously. 
8. Firmware upgrade – The manufacturer shall offer a program capable of upgrading multiple cameras at the same time (not requiring access to individual cameras).
9. Camera backup setting – The manufacturer shall provide a program that provides the ability to save multiple camera settings to a file and restore these camera settings if needed.
10. Reporting – The manufacturer shall provide a tool that can generate a report including thumbnail view, MAC address, IP address, serial number and other camera settings.
I. Electrical
1. Power
a. Input Voltage / Current	24V AC
b. Power Consumption:	24V AC : Max. 99W(Camera)
24V AC : Max. 50W(IR)
J. Mechanical And Environmental
1. Material: 
a. Color:			Metallic Silver
b. Material:			Stainless 316L
2. Dimensions (W x H):		611.0 x 438.0 x 235.0 mm (24.06 x 17.24 x 9.25 in.) 
3. Weight 				36kg (79.37 lb.)
4. Temperature: 		
a. Operating: 			-40° C to 60° C (-40° F to 140° F)
b. Storage:  			-30° C to 60° C (-22° F to 140° F)
5. Humidity:			0 - 95%, non-condensing
6. Environmental Rating:	
a. Mechanical (Vandal) Protection		IK10
b. Ingress Protection				IP67
7. Explosion proof
a. IECEx			Ex DB  IIC T6 Gb Ex tb IIIC T80 ℃ Db
b. ATEx			CE2460 EX II 2 GD Ex d IIC T6 Gb IP67 Ex tb IIIC T80°C Db


END OF SECTION


PART  2    EXECUTION
2.01 INSTALLERS
A. Contractor personnel shall comply with all applicable state and local licensing requirements.
2.02 PREPARATION
A. The network design and configuration shall be verified for compatibility and performance with the camera(s). 
B. Network configuration shall be tested and qualified by the Contractor prior to camera installation.
C. All firmware found in products shall be the latest and most up-to-date provided by the manufacturer, or of a version as specified by the provider of the Video Management Application (VMA) or Network Video Recorder (NVR). 
D. All equipment requiring users to log on using a password shall be configured with user/site-specific password/passwords. No system/product default passwords shall be allowed.
2.03 INSTALLATION
A. The Contractor shall carefully follow instructions in documentation provided by the manufacturer to insure all steps have been taken to provide a reliable, easy-to-operate system.
B. All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.
C. Before permanent installation of the system, the Contractor shall test the system in conditions simulating the final installed environment.
2.04 STORAGE
A. The hardware shall be stored in an environment where temperature and humidity are in the range specified by the Manufacturer.
 
END OF SECTION
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