Hanwha Vision is a leading supplier of advanced video surveillance solutions for IP-video, analog and hybrid systems. Building on the company's history of innovation, Hanwha Vision is dedicated to providing systems solutions with the highest levels of performance, reliability and cost-efficiency. Hanwha Vision is committed to the continued development of innovative systems products for professional security applications.

For additional information, visit https://www.hanwhavision.com/en/, https://hanwhavisionamerica.com

- PRODUCTS

  - EQUIPMENT

    - Model: X100

    - Alternates: none

  - ACCESS CONTROL REMOTE DEVICES

    - The family of intelligent controllers and peripheral interface devices must provide an open architecture family of products that enables a choice of host software system vendor without replacement of hardware.

    - The peripheral interface device shall control two physical barriers and up to four (using OSDP) or two (using Wiegand) readers.

    - The peripheral interface device shall support a wide range of reader technologies and protocol/electrical signaling standards, including OSDP (RS-485), OSDP SC (RS-485), Wiegand (TTL), magnetic stripe, F/2F and biometric. Wiegand and magnetic strip protocols must support one or two wire LED controls, and buzzer control.

    - The reader ports of the peripheral interface device shall be capable of supporting multi-dropped OSDP readers.

    - The peripheral interface device shall be able to utilize a cryptographic module that can encrypt/decrypt communication with the intelligent controller, supporting AES encryption using a minimum 256 bit key length.

    - The peripheral interface device shall utilize a crypto memory chip that provides hardened protection of secrets such as OSDP secure channel keys.

1.03    TECHNICAL SPECIFICATIONS

A.  The X100 is for use in low voltage, Class 2 circuits only

B.  The installation of this device must comply with all local fire and electrical codes.

C.  Primary Power: 12 to 24 Vdc ± 10 %, 1.5A (340 mA excluding readers)

D.  Communication with Intelligent Controller: 2-wire RS-485 2,400 to 115,200 bps, asynchronous,

half-duplex, 1 start bit, 8 data bits, and 1 stop bit

E.  Inputs: Seven unsupervised/supervised, standard EOL: 1k/1k ohm, 1%, ¼ watt (includes TAMPER, AC

FAIL and BATT FAIL inputs)

        - Outputs: Four relays, Form-C with dry contacts

- Normally open contact (NO): 5 A @ 30 Vdc resistive

- Normally closed contact (NC): 3 A @ 30 Vdc resistive

F.  Reader Interface

1. Reader Power: 12 Vdc ± 10 % regulated, 500 mA maximum for each reader

2. Data Inputs: TTL compatible or two wire RS-485 standards supported. Maximum cable length

(TTL/Wiegand): 500 ft. (152 m)

3. OSDP (RS-485) Mode: 9,600 to 230,400 bps, asynchronous, half-duplex, 1 start bit, 8 data bits, and

1 stop bit. Maximum cable length: 2000 ft. (609.6 m)

4. LED & Buzzer Output: 12 Vdc open circuit maximum, 40 mA sink maximum

G. Cable requirements

1. Readers-OSDP: 4 conductor twisted pair over-all shield. 2000 ft (610 m) maximum. Utilize one pair

for data and one pair for power.

2. Readers-Wiegand/C&D: 4-conductor, 18 AWG, shielded, 500 ft (150 m) maximum)

3. IO Module: One twisted pair, shielded, 24 AWG, 120 ohm impedance, 4,000 ft (1,219 m) maximum

4. Alarm Inputs: One twisted pair per input, 30 ohms maximum, typically 22 AWG, 1000 ft. (304.8 m)

5. Power and Relays: 2-conductor shielded, 18 to 16 AWG, 500 ft (150 m)

H. Environmental

1. Temperature:

ⅰ. Operating: 32 to 158°F (0 to +70°C)

ⅱ. Storage: -67 to 185°F (-55 to +85°C)

      - Humidity: 5 to 85% RHNC

- Mechanical:

1. Dimension: 6.46” x 5.51” x 1.02” (164 mm x 140 mm x 26 mm)

2. Weight: 342g

J. Product Compliance

1. FCC Part 15 Subpart B

2. CE

3. BSMI

4. IC

5. AS/NZS

6. TCVN

7. KCC

8. VCCI

9. UL-294 Recognized Component

10. IEC 62368-1

11. CB Scheme

12. RoHS (2011/65/EU & 2015/863)

13. EU REACH (1907/2006)

14. California Proposition 65

K. Warranty: HID Global warrants the product is free from defects in material and workmanship under normal

use and service with proper maintenance for two years from the date of factory shipment.

1.04.    TECHNICAL FEATURES

A. Card Formats:

1. Eight active card formats per intelligent controller

2. 19 digit (64-bit) User ID and 15 digit PIN numbers maximum

B. Door Control:

1.   Multiple card format support by reader

2.   Paired reader support

3.   Alternate reader support

4.   Elevator support

5.   Turnstile support

6.   Open Supervised Device Protocol (OSDP) and OSDP SC compliant

7.   Occupancy count

8.   Support of multi-occupancy rules

9.   Anti-passback support

ⅰ. Area-based, reader-based, or time based

ⅱ. Nested area, hard, soft, or timed forgiveness

10.   Supports host-based approval rules

11.   Keypad support with programmable user commands, card input

12.  Shunt relay support

13.  Strike follower relay support

14.  Threat level and Operating Modes

15.  Host controlled OSDP reader passthrough

16.  Elevator floor override

C.   Database Functions:

1.   Supports card numbers up to 64-bits in length

D. Offline mode operation

1.    Door mode

ⅰ. Unlocked, locked, facility code only

2.    Relay Mode

ⅰ. Programmable for offline conditions

END OF SECTION

8