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For additional information, visit https://www.hanwhavision.com/en/, https://hanwhavisionamerica.com



PART  1  PRODUCTS
1.01 EQUIPMENT
A. Model: X200
B. Alternates: none
1.02 ACCESS CONTROL REMOTE DEVICES
A. The family of intelligent controllers and peripheral interface devices must provide an open architecture family of products that enables a choice of host software system vendor without replacement of hardware.
B. The peripheral interface device shall be used to monitor nineteen (19) inputs and control two (2) outputs.
C. The peripheral interface device shall be able to utilize a cryptographic module that can encrypt/decrypt communication with the intelligent controller, supporting AES encryption using a minimum 256 bit key length.
D. The peripheral interface device shall utilize a crypto memory chip that provides hardened protection of secrets such keys.
1.03    TECHNICAL SPECIFICATIONS
            A.  The X200 is for use in low voltage, Class 2 circuits only
            B.  The installation of this device must comply with all local fire and electrical codes.
            C.  Primary Power: 12 to 24 Vdc ± 10 %, 300mA
            D.  Communication with Intelligent Controller: 2-wire RS-485 2,400 to 115,200 bps, asynchronous, 
                  half-duplex, 1 start bit, 8 data bits, and 1 stop bit 
            E.   Inputs: 19 unsupervised/supervised, standard EOL: 1k/1k ohm, 1%, ¼ watt (includes TAMPER, AC 
FAIL and BATT FAIL inputs). UL evaluation for access control use only.
F.  Outputs: Two Form-C relays. Contact rating: 2A @ 30 Vdc resistive
           G. Cable requirements
                 1. IO Module: One twisted pair, shielded, 24 AWG, 120 ohm impedance, 4,000 ft (1,219 m) maximum
                 2. Alarm Inputs: One twisted pair per input, 30 ohms maximum, typically 22 AWG, 1000 ft. (304.8 m)
                 3. Relay outputs: As required for the load
                 4. Power: 2-conductor shielded, 18 to 16 AWG, 500 ft (150 m) 
             H. Environmental
                  1. Temperature:
ⅰ. Operating: 32 to 158°F (0 to +70°C)
ⅱ. Storage: -67 to 185°F (-55 to +85°C)
2. Humidity: 5 to 85% RHNC
I. Mechanical:
1. Dimension: 6.46” x 5.51” x 1.02” (164 mm x 140 mm x 26 mm)
2. Weight: 326g
            J. Product Compliance
                   1. FCC Part 15 Subpart B
                   2. CE
                   3. BSMI
                   4. IC
                   5. AS/NZS
                   6. TCVN
                   7. KCC
                   8. VCCI
                   9. UL-294 Recognized Component
                  10. IEC 62368-1
                 11. CB Scheme
                 12. RoHS (2011/65/EU & 2015/863)
                 13. EU REACH (1907/2006)
                 14. California Proposition 65
            K. Warranty: HID Global warrants the product is free from defects in material and workmanship under normal
                use and service with proper maintenance for two years from the date of factory shipment.
            L. Offline mode operation
                 1. Relay mode
                    ⅰ. Programmable for offline conditions 
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